Email: info@uapc.com

1140 KINGWOOD AVENUE - NORFOLK, VA 23502	TEL: 757-461-0077 • FAX: 757-461-0808

4715 STOCKHOLM COURT - CHARLOTTE, NC 28273                       TEL: 704-374-0600 • FAX: 704-374-1008

Quality Equipment and Service Since 1962

Universal Air & Gas Products Corporation (UAPC)

Standard Submittal Data as of  10/01/2000

Model: 	C3-30H1  (Optional Spray Wash Manifolds)

General:

Each two-stage, dry, electrostatic precipitator shall be a Universal Air & Gas Products Corporation Model C3-30H1, specifically designed for commercial or light industrial applications.  The air cleaner shall be rated for 3000 scfm with ASHRAE efficiency of 96% DOP on 0.01 micron or greater particulate.

Cabinet Enclosure:

Each C3-30H1 shall house three (3) each, 1000 cfm rated electrostatic cell.  The cells shall be arranged three (3) to a row, in a on (1) cell high configuration.  Each cell shall slide easily into the cabinet enclosure on reinforced, steel support  frames.  The cabinet enclosure shall be constructed of 16 gauge, galvanized steel.  Access to the cell shall be available through a front access panel, which can be latched in place while in service, or unlatched and lifted off for cell access.  Intake and discharge openings shall accommodate horizontal air flow through the top of the air cleaner, from left to right when facing the access panel opening.  (Right to left flow is available, if specified.)  Inlet and outlet openings are dimensioned per the C3-30H1 general arrangement drawings and are sized to accommodate less than 405 feet per minute air velocity at rated capacity.  A 2”, flanged lip for connection of inlet and discharge ductwork shall be provided on both inlet and discharge opening edges.  The floor pan of the air cleaner cabinet shall be equipped with a 2”, NPTf, cast iron, floor flange for drainage of cleaning water. The floor pan will be three (3”) inches deep and rendered water tight by means of seal welded corners.  One (1) each, 6” high, steel mounting foot is welded to each of the four corners of the cabinet floor pan to provide clearance for drainage water piping installed by others.

Water wash Manifold: (Optional)

The 2” inlet and discharge cabinet lip shall be equipped with holes for mounting of one (1) each, ¾” copper pipe, which incorporates 14, wide angle, brass, spray header nozzles per 1000 cfm cell, totaling 42 nozzles. Spray headers shall be mounted at the factory on the inlet side of the air cleaner only, with holes provided for mounting of optional spray headers on the outlet side of the cabinet.  Water flow per manifold connection is recommended at  29 gpm, 40 PSI.  (See optional water wash control system.)

Air Cleaner Cell:

Each air cleaner cell shall be a Universal Air & Gas Products model C1000, industrial, 2-stage, dry, precipitator rated for 1000 cfm at  96% DOP, ASHRAE efficiency at 0.01 micron.  Each cell shall have an integral ionizing section incorporating 13 each, 0.007 inch diameter, tungsten electrodes suspended at each end by stainless steel springs attached to a high voltage support bar.  The high voltage support bar shall be suspended without insulators by a rigid aluminum frame.  Each cell shall utilize 27 ground collector plates, providing 9,688 square inches of surface area, and 28 high voltage collector plates providing 8,824 square inches of surface area.  Alternating ground and high voltage collector plates shall be separated by 0.323 inches by means of individually removable, aluminum spacers bored and machined to a 0.005” tolerance from rod stocks.  Both collector and high voltage plates shall be supported by a total of 8, ¼” aluminum tie rods threaded at each end of ¼-20NC.  Both ionizer and collector sections

MANUFACTURER/DESIGNER OF AIR/GAS COMPRESSOR SYSTEMS, ELECTROSTATIC PRECIPITATOR SYSTEMS

AND RELATED CONTROLS AND ACCESSORIES

shall operate normally at 8000 VDC with a voltage gradient of 11,158 VDC in the ionizer section, and 24,768 VDC in the collector section.  The high voltage plates shall be isolated from the ground plates by means of UAPC proprietary design, 2½” diameter, glazed ceramic insulators.   Cell lifting handles are provided at each end of the cell.  Each cell shall weigh 32 lbs., is all aluminum in collector plate and tie rod support construction, and measures 18” height x 21¼” wide x 12-9/16” deep. Twenty-four (24”) inches of clearance is recommended on the access panel side, for ease of cell removal and general system service.

Air Cleaner Power Pack:

Each tier consists of  three (3) each, 1000 cfm cells, and shall be powered by a single, solid state power supply.  Each power supply shall incorporate a single, copper wound transformer as manufactured by Universal Air & Gas Products.  Each transformer shall require 120VAC, single phase, 60 Hz primary voltage and deliver 7200-8800 volts AC capable to 5.0 mA.  Transformer output shall be rectified by a single, silicon diode rectifier supported by glazed, ceramic insulators.  Other power pack components shall include a 0.8 mA circuit breaker with manual reset; green LED, power-on light, milliammeter with operating range identified between 1.5 to 2.1 mA; 125 ohm, variable rheostat; safety door interlock switch which cuts all power to the air cleaner cell if the power pack lid is opened; high voltage bleeder resistor; capacitor.  A grounded, 120VAC power cord with plug is provided with each power pack. The power pack enclosure shall be 16 gauge, cold rolled steel with prime coat and enamel finish.  The power packs are system mounted as standard for indoor service.  For outdoor service, optional  remote mounting wall brackets are provided with NEMA 4 conduit boxes installed at each electrical connection required on the air cleaner cabinet.  Power is transmitted from the power pack to a cell via a thru-panel, ceramic bushing assembly mounted on the removable, cabinet access panel.  Power is transmitted between cells by means of stainless steel, heat-treated (spring) jumpers.

Mechanical Post Filters:

Mounting rails are provided for three (3) each, 1” thick, cleanable, aluminum mesh, post filter (one for each 1000 cfm cell).  Post filters are provided to allow for sufficient back pressure (0.10” wg) for even air flow across the cell surface area and to provide a backstop water overspray during the cleaning process from the inlet  side of the cell.  If outlet side cleaning is required, or if inlet side pre-filtration is required, then special filter collars are required.  Consult factory for these optional features.

Total system weight: per attached drawing.

Total system dimension: per attached drawing.

Accessories and Options Available:

(	Inlet and discharge filter racks and plenums

(	Control A, Control A-1 wash system

(	Dual side wash manifolds

(	Detergent pump system

(	Remote mounting power pack kits

(	Custom designed control systems

(	Custom designed cabinets

(	Special materials of construction for cells or cabinets

(	System packaging of air cleaners with other components as specified on a common structural base 	frame

(	Special finish painting