Email: info@uapc.com

1140 KINGWOOD AVENUE - NORFOLK, VA 23502	TEL: 757-461-0077 • FAX: 757-461-0808

4715 STOCKHOLM COURT - CHARLOTTE, NC 28273                       TEL: 704-374-0600 • FAX: 704-374-1008

Quality Equipment and Service Since 1962

Universal Air Products Corporation (UAPC)

Standard Submittal Data as of  10/01/2000

Model: 	Mi-20H1  (Optional Spray Wash Manifolds)

General:

Each two-stage, dry, electrostatic precipitator shall be a Universal Air Products Corporation Model Mi-20H1, specifically designed for industrial, self-contained applications.  The air cleaner shall be rated for 2000 scfm with an ASHRAE efficiency of 96% DOP on 0.01 micron or greater particulate.

Cabinet Enclosure:

Each Mi-20H1 shall house two (2) each, 1000 cfm rated electrostatic cell.  The cells shall be arranged two (2) to a row, in a one (1) cell high configuration.  Each cell shall slide easily into the cabinet enclosure on reinforced, steel support frames.  The cabinet enclosure shall be constructed of 16 gauge, steel, primed and finish coated in blue enamel paint.  Access to the cell shall be available through a hinged, front access panel.  The access panel can be latched in place while in service, or unlatched and swung open for cell access.  Intake and discharge openings shall accommodate horizontal airflow through the air cleaner, from left to right when facing the access panel opening.  Inlet and outlet openings are dimensioned per the Mi20H1 general arrangement drawing and are sized to accommodate less than 405 feet per minute air velocity at rated capacity.  The floor pan of the air cleaner cabinet can be equipped with an optional 2”, NPTf, cast iron, floor flange for drainage of cleaning water or collected fluids. The floor pan shall be two (2”) inches deep and is rendered water tight by means of seal welded seams.

Blower and Motor Compartment:

Each Mi-20H1 shall be equipped with a NEMA, ODP, 1/2 HP motor, which drives a forward curve type blower assembly.  The V-belt drive maintains a 800 RPM blower speed.  The motor can be supplied with 115V or 230V, single phase, 60Hz power. Optional 50Hz, three phase and alternative voltages or motor design types are available at added cost upon request.  The blower and motor assemblies are mounted down stream of the air cleaner’s cell, in order that air can be pulled through the air cleaner’s cell.  The entire blower and motor compartment is housed within the cabinet enclosure as described above.  Blower and motor sizes are selected based upon and assumed ambient, blank intake and discharge opening, which is unattached to external ductwork.  In the event that external ductwork is to be added at the intake or discharge side of the air cleaner, then blower and motor sizes must be increased to accommodate the added static pressure drop through the system.  Typically, a larger blower and motor assembly is required at added cost, if normal static pressure drop through the air cleaner is increased.

Water-wash Manifold: (Optional)

The interior of the cabinet shall be equipped with deflector panels designed to prevent wash over-spray from entering the blower and motor compartment of the unit.  Holes are provided for mounting one (1) each, ¾” copper pipe, which incorporates 14, wide angle, brass, spray header nozzles per 1000 cfm cell. Spray headers shall be mounted at the factory for the inlet or discharge side of the air cleaner.  Outlet side spray manifolds also require the installation of an inlet plenum to the air cleaner unit, which is designed to capture wash water over-spray and return it to the drain pan. Water flow per manifold connection is recommended at 20 GPM @ 40 PSI.  (See optional water wash control system.)

Air Cleaner Cell:

Each air cleaner cell shall be a Universal Air Products model i1000, industrial, 2-stage, dry, precipitator

MANUFACTURER/DESIGNER OF AIR/GAS COMPRESSOR SYSTEMS, ELECTROSTATIC PRECIPITATOR SYSTEMS AND RELATED CONTROLS AND ACCESSORIES

rated for 1000 cfm at  96% DOP, ASHRAE efficiency at 0.01 micron.  Each cell shall have an integral ionizing section incorporating 13 each, 0.007 inch diameter, tungsten electrodes suspended at each end by stainless steel springs attached to a high voltage support bar.  The high voltage support bar shall be suspended without insulators by a rigid aluminum frame.  Each cell shall utilize 27 ground collector plates, providing 9,688 square inches of surface area, and 28 high voltage collector plates providing 8,824 square inches of surface area.  Alternating ground and high voltage collector plates shall be separated by 0.323 inches by means of individually removable, aluminum spacers bored and machined to a 0.005” tolerance from rod stocks.  Both collector and high voltage plates shall be supported by a total of 12, ¼” aluminum tie rods threaded at each end of ¼-20NC.  Both ionizer and collector sections shall operate normally at 8000 VDC with a voltage gradient of 11,158 VDC in the ionizer section, and 24,768 VDC in the collector section.  The high voltage plates shall be isolated from the ground plates by means of UAPC proprietary design, 2½” diameter, glazed ceramic insulators.   Cell lifting handles are provided at each end of the cell.  Each cell shall weigh 32 lbs., is all aluminum in collector plate and tie rod support construction, and measures 18” height x 21-1/4” wide x 12-9/16” deep.  Twenty-eight (28”) inches of clearance is recommended on the access panel side, for ease of cell removal and general system service.

Air Cleaner Power Pack:

Each tier consists of (2) each, 1000 cfm cells and shall be powered by a single, solid state power supply.  Each power supply shall incorporate a single, copper wound transformer as manufactured by Universal Air Products.  Each transformer shall require 120VAC, single phase, 60 Hz primary voltage and deliver 7200-8800 volts AC capable to 5.0 mA.  Transformer output shall be rectified by a single, silicon diode rectifier supported by glazed, ceramic insulators.  Other power pack components shall include a 0.6 mA circuit breaker with manual reset; green LED, power-on light, milliammeter with operating range identified between 1.1 to 1.7 mA; 125 ohm, variable rheostat; safety door interlock switch, which cuts all power to the air cleaner cell if the power pack lid is opened; high voltage bleeder resistor; capacitor.  A grounded, 120VAC power cord with plug is provided with each power pack. The power pack enclosure shall be 16 gauge, cold rolled steel with prime coat and enamel finish.  The power packs are system mounted as standard for indoor service.  Mi-series units are intended for indoor, NEMA 1 or NEMA 12 rated service. Since units are normally suspended from the ceiling, optional remote mounting of the power pack is recommended at added cost.  Optional remote mounting wall brackets are provided with NEMA 12 conduit boxes installed at each electrical connection required on the air cleaner’s cabinet.  Power is transmitted from the power pack to a cell via a thru-panel, ceramic bushing assembly mounted on the hinged, cabinet access panel.  For units with more than one cell per tier, power is transmitted between cells by means of stainless steel, heat-treated (spring) jumper.

Mechanical Post Filters:

Mounting rails are provided for two (2) each, 1” thick, cleanable, aluminum mesh, post filter (one for each 1000 cfm cell).  Post filters are provided to allow for sufficient back pressure (0.10” wg) for even air flow across the cell surface area and to provide a backstop for water over-spray during the cleaning process from the inlet side of the cell.  If outlet side cleaning is required, or if inlet side pre-filtration is required, then special filter collars are required at added cost.  Consult factory for these optional features.

Total system weight: per attached drawing.

Total system dimension: per attached drawing.

Accessories and Options Available:

(	Inlet and discharge filter racks and plenums

(	Control A, Control A-1 wash system

(	Dual side wash manifolds

(	Detergent pump system

(	Remote mounting power pack kits

(	Custom designed control systems

(	Custom designed cabinets

(	Special materials of construction for cells or cabinets

(	System packaging of air cleaners with other components as specified

(	Special finish painting